Master HE
MHE 200
INPUT		
Rated power	200000 VA	
Voltage	400 Vac three-phase Vac	
Voltage tolerance	+ 20% - 25%	
Frequency	50/60 Hz with autorange	
Frequency tolerance	45/65 Hz	
Power factor	0,99	
Input current	281 A	
Current distorsion	<3%	
Soft start	0-100% in 10	
BY PASS		
Rated voltage	400 Vac three-phase selectable 380 and 415	
Voltage tolerance	± 15% (selectable from ± 10% to ± 25% from front panel)	
Rated frequency	50/60 Hz (autorange)	
Frequency tolerance	± 2% (selectable from ± 1% to ± 5% from front panel)	
Rated current	281 A	
Number phases	3	
Back-feed protection	yes 	
Overload capacity Inx10ms	14	
OUTPUT and INVERTER OUTPUT		
Rated power	200000 VA	
Active power	200000 W	
Number phases	3 + N	
Crest factor (Ipeak/Irms)	3 : 1	
Waveform	Sinewave	
Dynamic stability	± 5% in 5 ms	
Frequency	same as the input (autorange)	
Voltage distortion with distorcing load	<3%	
Voltage distortion with linear load	<1%	
Frequency stability	± 0,05% on mains failure ± 2% (selectable from ± 1% to ± 5% from front panel) with mains supply present	
Overload	125% 150% 200% of the rated current for 10' / 1' / 7	
RECTIFIER OUTPUT		
Ripple	<1%	
BATTERIES		
Type	Maintenance-free sealed lead-acid	
Maximum recharge current	0.2xC10	
ENVIRONMENTAL		
Altitude max	1000 m	
Color	Dark grey RAL 7035	
Remote controls	EPO and bypass	
Safety compliance	EN 62040-1	
EMC conformance	EN 62040-2 Directives 73/23-93/68-89/336 EEC EN 62040-3	
Protection rating	3	
Line-Interactive/Smart Active efficiency	up to 99,4%	
Noise	63 dBA at 1 m	
Remote signals	voltage free contacts (mains power failure, UPS on bypass, end of discharge pre-alarm, output 12Vdc 80mA)	
Operating temperature	0 ÷ 40 °C	
Relative humidity	95% no condensing	
DATA		
Weight	910 Kg	
Dimensions (h w d)	1900x1000x850 mm